## Sheet1
Design Conditions |  |  |  |  | External Wall Specifications | [7 empty] | Partation Wall Specifications
Latitude | 27.7° |  |  |  | Code No | Thickness inch | Description |  |  | Resistance | U |  | Code No | Thickness inch | Description |  |  | Resistance | U
Dry bulb Temperature(°F) | 89 |  |  |  | A0 |  | Outside surface resistence |  |  | 0.33 | 3.0303 |  | E0 |  | Inside surface resistence |  |  | 0.61 | 1.6393
Wet bulb temperature (°F) | 78 |  |  |  | E1 | 3/4" | 3/4" Plaster or Gypsum |  |  | 0.15 | 6.6667 |  | E1 | 3/4" | 3/4" Plaster or Gypsum |  |  | 0.15 | 6.6667
Daily Range (°F) | 25 |  |  |  | C8 | 8" | 8" Heavyweight Concrete Block |  |  | 1.11 | 0.9009 |  | C4 | 4" | 4" Common Brick |  |  | 1.59 | 0.62893
Indoor Temperature (°F) | 84 |  |  |  | E1 | 3/4" | 3/4" Plaster or Gypsum |  |  | 0.15 | 6.6667 |  | E1 | 3/4" | 3/4" Plaster or Gypsum |  |  | 0.15 | 6.6667
Desired Indoor Temperatute (°F) | 68 |  |  |  | E0 |  | Inside surface resistence |  |  | 0.61 | 1.6393 |  | E0 |  | Inside surface resistence |  |  | 0.61 | 1.6393
tm (°F) | 76.5 |  |  |  | Total |  |  |  |  | 2.35 | 0.42553 |  | Total |  |  |  |  | 3.11 | 0.32154
Conduction correction | 1.5
[9 empty] | Top Floor Window description | [10 empty] | Window Specifications
Roof Specifications | [8 empty] | Window | Facing | No of interior walls | Floor Covering | Partition type | Inside Shade | Zone type |  |  |  |  | Double Glazing | e=0.2
Code No | Thickness inch | Description |  |  |  | Resistance | U |  | Toilet 2 (W2) | North | 3 | Vinyl | Concrete block | None | C |  |  |  |  | Air space | 1/4"
A0 |  | Outside surface resistence |  |  |  | 0.33 | 3.0303 |  | Bedroom 2 (W) | North | 2 | Vinyl | Concrete block | None | D |  |  |  |  | Vertical Installation | Fixed | Aluminium with thermal break
E1 | 3/4" | 3/4" Plaster or Gypsum |  |  |  | 0.15 | 6.6667 |  | Puja (W1) | North | 3 | Vinyl | Concrete block | None | C |  |  |  |  | U value | 0.54
C12 | 8" | 2" Heavyweight Concrete Block |  |  |  | 0.17 | 5.8824 |  | Bedroom 1 (W) | South | 2 | Vinyl | Concrete block | None | D
E1 | 3/4" | 3/4" Plaster or Gypsum |  |  |  | 0.15 | 6.6667 |  | Toilet 1(W2) | East | 2 | Vinyl | Concrete block | None | D
E0 |  | Inside surface resistence |  |  |  | 0.61 | 1.6393 |  | Bedroom 1 (W1) | East | 2 | Vinyl | Concrete block | None | D
Total | [5 empty] | 1.41 | 0.70922 |  | Passage(W1) | East | 3 | Vinyl | Concrete block | None | C
[9 empty] | Passage(W1) | South | 3 | Vinyl | Concrete block | None | C
[9 empty] | Passage(W1) | South | 3 | Vinyl | Concrete block | None | C
GROUND FLOOR
Room | Ceiling |  |  | Volume | East | [5 empty] | North | [5 empty] | West | [5 empty] | South
| Length | Breadth | Area |  | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area
Kitchen | 11.167 | 12.83 | 143.2726 | 1277.5189 | 12.83 | 8.9167 | 114.4013 | W | 27 | 87.4013 | 11.167 | 8.9167 | 99.5728 | D | 22.75 | 76.8228 | 12.83 | 8.9167 | 114.4013 | - | 0 | 114.4013 | 11.167 | 8.9167 | 99.5728 | W | 27 | 72.5728
Bedroom 1 | 11.25 | 12.25 | 137.8125 | 1228.8327 | 12.25 | 8.9167 | 109.2296 | - | 0 | 109.2296 | 11.25 | 8.9167 | 100.3129 | D | 22.75 | 77.5629 | 12.25 | 8.9167 | 109.2296 | - | 0 | 109.2296 | 11.25 | 8.9167 | 100.3129 | W | 27 | 73.3129
Toilet | 7.58 | 4.38 | 33.2004 | 296.038 | 4.38 | 8.9167 | 39.0551 | D1 | 19.25 | 19.8051 | 7.58 | 8.9167 | 67.5886 | W2 | 7.875 | 59.7136 | 4.38 | 8.9167 | 39.0551 | - | 0 | 39.0551 | 7.58 | 8.9167 | 67.5886 | - | 0 | 67.5886
Bedroom 2 | 10.167 | 9.5 | 96.5865 | 861.2328 | 9.5 | 8.9167 | 84.7087 | - | 0 | 84.7087 | 10.167 | 8.9167 | 90.6561 | W | 27 | 63.6561 | 9.5 | 8.9167 | 84.7087 | - | 0 | 84.7087 | 10.167 | 8.9167 | 90.6561 | D | 22.75 | 67.9061
Living Room | 10.83 | 12.5 | 135.375 | 1207.0983 | 12.5 | 8.9167 | 111.4587 | D | 22.75 | 88.7087 | 10.83 | 8.9167 | 96.5679 | W | 27 | 69.5679 | 12.5 | 8.9167 | 111.4587 | P | 37.1559 | 74.3029 | 10.83 | 8.9167 | 96.5679 | D | 22.75 | 73.8179
Passage | 3.25 | 4.167 | 13.5427 | 120.7566 | 4.167 | 8.9167 | 37.1559 | P |  | 37.1559 | 3.25 | 8.9167 | 28.9793 | D | 22.75 | 6.2293 | 4.167 | 8.9167 | 37.1559 | D1 | 19.25 | 17.9059 | 3.25 | 8.9167 | 28.9793 | D | 22.75 | 6.2293
FIRST FLOOR
Room | Ceiling |  |  | Volume | East | [5 empty] | North | [5 empty] | West | [5 empty] | South
| Length | Breadth | Area |  | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area
Bedroom | 15.5 | 12.833 | 198.9115 | 1773.6342 | 12.833 | 8.9167 | 114.428 | - | 0 | 114.428 | 15.5 | 8.9167 | 138.2089 | D,D1 | 42 | 96.2088 | 12.833 | 8.9167 | 114.428 | - | 0 | 114.428 | 15.5 | 8.9167 | 138.2089 | SD | 45 | 93.2088
Living Room | 14.75 | 12.5 | 184.375 | 1644.0166 | 12.5 | 8.9167 | 111.4587 | D | 22.75 | 88.7087 | 14.75 | 8.9167 | 131.5213 | W | 27 | 104.5213 | 12.5 | 8.9167 | 111.4587 | D1 | 19.25 | 92.2087 | 14.75 | 8.9167 | 131.5213 | D,D | 45.5 | 86.0213
Kitchen/Dinning | 17.167 | 8.75 | 150.2113 | 1339.3887 | 8.75 | 8.9167 | 78.0211 | W | 27 | 51.0211 | 17.167 | 8.9167 | 153.073 | P | 59.4261 | 93.6469 | 8.75 | 8.9167 | 78.0211 | - | 0 | 78.0211 | 17.167 | 8.9167 | 153.073 | W1,SD | 76 | 77.073
Toilet 1 | 8 | 5.4167 | 43.3336 | 386.3927 | 5.4167 | 8.9167 | 48.2991 | - | 0 | 48.2991 | 8 | 8.9167 | 71.3336 | W2 | 7.875 | 63.4586 | 5.4167 | 8.9167 | 48.2991 | - | 0 | 48.2991 | 8 | 8.9167 | 71.3336 | D1 | 19.25 | 52.0836
Toilet 2 | 5.4167 | 8 | 43.3336 | 386.3927 | 8 | 8.9167 | 71.3336 | D1 | 19.25 | 52.0836 | 5.4167 | 8.9167 | 48.2991 | W2 | 7.875 | 40.4241 | 8 | 8.9167 | 71.3336 | - | 0 | 71.3336 | 5.4167 | 8.9167 | 48.2991 | - | 0 | 48.2991
Store | 8.83 | 5 | 44.15 | 393.6723 | 5 | 8.9167 | 44.5835 | W2 | 7.875 | 36.7085 | 8.83 | 8.9167 | 78.7345 | - | 0 | 78.7345 | 5 | 8.9167 | 44.5835 | D1 | 19.25 | 25.3335 | 8.83 | 8.9167 | 78.7345 | - | 0 | 78.7345
Passage | 7.25 | 5 | 36.25 | 323.2304 | 5 | 8.9167 | 44.5835 | D1 | 19.25 | 25.3335 | 7.25 | 8.9167 | 64.6461 | D | 22.75 | 41.8961 | 5 | 8.9167 | 44.5835 | - |  | 44.5835 | 7.25 | 8.1967 | 59.4261 |  |  | 59.4261
TOP FLOOR
Room | Ceiling |  |  | Volume | East | [5 empty] | North | [5 empty] | West | [5 empty] | South
| Length | Breadth | Area |  | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area | Length | Height | Area | Window/Door | Area | Net Area
Bedroom 1 | 11.25 | 12.25 | 137.8125 | 1228.8327 | 12.25 | 8.9167 | 109.2296 | W | 27 | 82.2296 | 11.25 | 8.9167 | 100.3129 | D1 | 19.25 | 81.0629 | 12.25 | 8.9167 | 109.2296 | - |  | 109.2296 | 11.25 | 8.9167 | 100.3129 | W | 27 | 73.3129
Bedroom 2 | 14.25 | 9.5 | 135.375 | 1207.0983 | 9.5 | 8.9167 | 84.7087 | - |  | 84.7087 | 14.25 | 8.9167 | 127.063 | W | 27 | 100.063 | 9.5 | 8.9167 | 84.7087 | - |  | 84.7087 | 14.25 | 8.9167 | 127.063 | D | 22.75 | 104.313
Puja | 6 | 8.33 | 49.98 | 445.6567 | 8.33 | 8.9167 | 74.2761 | - |  | 74.2761 | 6 | 8.9167 | 53.5002 | W1 | 31 | 22.5002 | 8.33 | 8.9167 | 74.2761 | - |  | 74.2761 | 6 | 8.9167 | 53.5002 | D1 | 19.25 | 34.2502
Store | 5.67 | 4 | 22.68 | 202.2308 | 4 | 8.9167 | 35.6668 | D | 22.75 | 12.9168 | 5.67 | 8.9167 | 50.5577 |  |  | 50.5577 | 4 | 8.9167 | 35.6668 |  |  | 35.6668 | 5.67 | 8.9167 | 50.5577 |  |  | 50.5577
Toilet 1 | 5 | 6.5 | 32.5 | 289.7928 | 6.5 | 8.9167 | 57.9586 | W2 | 7.875 | 50.0836 | 5 | 8.9167 | 44.5835 | D1 | 19.25 | 25.3335 | 6.5 | 8.9167 | 57.9586 | - |  | 57.9586 | 5 | 8.9167 | 44.5835 | - |  | 44.5835
Toilet 2 | 6.75 | 4.75 | 32.0625 | 285.8917 | 4.75 | 8.9167 | 42.3543 | - |  | 42.3543 | 6.75 | 8.9167 | 60.1877 | W2 | 7.875 | 52.3127 | 4.75 | 8.9167 | 42.3543 | - |  | 42.3543 | 6.75 | 8.9167 | 60.1877 | D1 | 19.25 | 40.9377
Passage | 16.33 | 4.41 | 72.0153 | 642.1388 | 4.41 | 8.9167 | 39.3226 | D | 22.75 | 16.5726 | 16.33 | 8.9167 | 145.6097 | D+D1 | 42 | 103.6097 | 4.41 | 8.9167 | 39.3226 | D | 22.75 | 16.5726 | 16.33 | 8.9167 | 145.6097 | D1 | 19.25 | 126.3597

## Load Calculation
CLTD CALCULATION FOR WALL
Ground Floor
Bedroom 2:West wall | [5 empty] | Bedroom 2:North Wall |  |  |  |  | Bedroom 1:West wall |  |  |  |  | Bedroom 1:South wall |  |  |  |  | Living Room : North Wall |  |  |  |  | Toilet : West wall |  |  |  |  | Kitchen/Dining: South Wall |  |  |  |  | Kitchen/Dining: East Wall
Time of day | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) |  |  |  |  | Rooms | U | A | ΔT | Q=U*A*ΔT(btu/hr)
10 | 0.42553 | 84.7087 | 4 | 5.5 | 198.2543 | 0.42553 | 63.6561 | 7 | 8.5 | 230.2454 | 0.42553 | 109.2296 | 4 | 5.5 | 255.6437 | 0.42553 | 73.3129 | 3 | 4.5 | 140.3864 | 0.42553 | 69.5679 | 7 | 8.5 | 251.6284 | 0.42553 | 39.0551 | 4 | 5.5 | 91.4057 | 0.42553 | 72.5728 | 3 | 4.5 | 138.9692 | 0.42553 | 87.4013 | 22 | 23.5 | 874.0126 |  |  |  |  | Kitchen | 0.70922 | 143.2726 | 16 | 1625.7885
11 | 0.42553 | 84.7087 | 6 | 7.5 | 270.3468 | 0.42553 | 63.6561 | 10 | 11.5 | 311.5085 | 0.42553 | 109.2296 | 6 | 7.5 | 348.605 | 0.42553 | 73.3129 | 5 | 6.5 | 202.7803 | 0.42553 | 69.5679 | 10 | 11.5 | 340.4385 | 0.42553 | 39.0551 | 6 | 7.5 | 124.6441 | 0.42553 | 72.5728 | 5 | 6.5 | 200.7332 | 0.42553 | 87.4013 | 31 | 32.5 | 1208.7408 |  |  |  |  | Bedroom 1 | 0.70922 | 137.8125 | 16 | 1563.8298
12 | 0.42553 | 84.7087 | 8 | 9.5 | 342.4392 | 0.42553 | 63.6561 | 12 | 13.5 | 365.6839 | 0.42553 | 109.2296 | 8 | 9.5 | 441.5664 | 0.42553 | 73.3129 | 7 | 8.5 | 265.1742 | 0.42553 | 69.5679 | 12 | 13.5 | 399.6452 | 0.42553 | 39.0551 | 8 | 9.5 | 157.8825 | 0.42553 | 72.5728 | 7 | 8.5 | 262.4973 | 0.42553 | 87.4013 | 36 | 37.5 | 1394.701 |  |  |  |  | Toilet | 0.70922 | 33.2004 | 16 | 376.7421
13 | 0.42553 | 84.7087 | 11 | 12.5 | 450.5779 | 0.42553 | 63.6561 | 14 | 15.5 | 419.8593 | 0.42553 | 109.2296 | 11 | 12.5 | 581.0084 | 0.42553 | 73.3129 | 11 | 12.5 | 389.9621 | 0.42553 | 69.5679 | 14 | 15.5 | 458.8518 | 0.42553 | 39.0551 | 11 | 12.5 | 207.7401 | 0.42553 | 72.5728 | 11 | 12.5 | 386.0255 | 0.42553 | 87.4013 | 39 | 40.5 | 1506.2771 |  |  |  |  | Bedroom 2 | 0.70922 | 96.5865 | 16 | 1096.017
14 | 0.42553 | 84.7087 | 15 | 16.5 | 594.7629 | 0.42553 | 63.6561 | 16 | 17.5 | 474.0347 | 0.42553 | 109.2296 | 15 | 16.5 | 766.9311 | 0.42553 | 73.3129 | 14 | 15.5 | 483.553 | 0.42553 | 69.5679 | 16 | 17.5 | 518.0585 | 0.42553 | 39.0551 | 15 | 16.5 | 274.217 | 0.42553 | 72.5728 | 14 | 15.5 | 478.6716 | 0.42553 | 87.4013 | 39 | 40.5 | 1506.2771 |  |  |  |  | LIving room | 0.70922 | 135.375 | 16 | 1536.1702
15 | 0.42553 | 84.7087 | 20 | 21.5 | 774.994 | 0.42553 | 63.6561 | 19 | 20.5 | 555.2978 | 0.42553 | 109.2296 | 20 | 21.5 | 999.3344 | 0.42553 | 73.3129 | 18 | 19.5 | 608.3409 | 0.42553 | 69.5679 | 19 | 20.5 | 606.8686 | 0.42553 | 39.0551 | 20 | 21.5 | 357.313 | 0.42553 | 72.5728 | 18 | 19.5 | 602.1997 | 0.42553 | 87.4013 | 37 | 38.5 | 1431.893
16 | 0.42553 | 84.7087 | 28 | 29.5 | 1063.3639 | 0.42553 | 63.6561 | 21 | 22.5 | 609.4732 | 0.42553 | 109.2296 | 28 | 29.5 | 1371.1798 | 0.42553 | 73.3129 | 20 | 21.5 | 670.7348 | 0.42553 | 69.5679 | 21 | 22.5 | 666.0753 | 0.42553 | 39.0551 | 28 | 29.5 | 490.2667 | 0.42553 | 72.5728 | 20 | 21.5 | 663.9638 | 0.42553 | 87.4013 | 36 | 37.5 | 1394.701
17 | 0.42553 | 84.7087 | 37 | 38.5 | 1387.78 | 0.42553 | 63.6561 | 23 | 24.5 | 663.6486 | 0.42553 | 109.2296 | 37 | 38.5 | 1789.5058 | 0.42553 | 73.3129 | 22 | 23.5 | 733.1287 | 0.42553 | 69.5679 | 23 | 24.5 | 725.282 | 0.42553 | 39.0551 | 37 | 38.5 | 639.8396 | 0.42553 | 72.5728 | 22 | 23.5 | 725.7279 | 0.42553 | 87.4013 | 35 | 36.5 | 1357.5089
First Floor
Bedroom :West wall | [5 empty] | Bedroom :South wall |  |  |  |  | Living Room : North wall |  |  |  |  | Kitchen/Dining: East Wall |  |  |  |  | Kitchen/Dining: South wall |  |  |  |  | Toilet 1 : West wall |  |  |  |  | Toilet 2 : West wall |  |  |  |  | Toilet 2 : North wall |  |  |  |  | Store : East wall | [6 empty] | Ceiling
Time of day | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) |  |  | Rooms | U | A | ΔT | Q=U*A*ΔT(btu/hr)
10 | 0.42553 | 114.428 | 4 | 5.5 | 267.8102 | 0.42553 | 93.2088 | 3 | 4.5 | 178.485 | 0.42553 | 104.5213 | 7 | 8.5 | 378.0559 | 0.42553 | 51.0211 | 22 | 23.5 | 510.2113 | 0.42553 | 77.073 | 3 | 4.5 | 147.5866 | 0.42553 | 48.2991 | 4 | 5.5 | 113.0404 | 0.42553 | 71.3336 | 4 | 5.5 | 166.951 | 0.42553 | 40.4241 | 7 | 8.5 | 146.2148 | 0.42553 | 36.7085 | 22 | 23.5 | 367.085 |  |  | Bedroom | 0.70922 | 198.9115 | 16 | 2257.1518
11 | 0.42553 | 114.428 | 6 | 7.5 | 365.1958 | 0.42553 | 93.2088 | 5 | 6.5 | 257.8117 | 0.42553 | 104.5213 | 10 | 11.5 | 511.4873 | 0.42553 | 51.0211 | 31 | 32.5 | 705.6113 | 0.42553 | 77.073 | 5 | 6.5 | 213.1806 | 0.42553 | 48.2991 | 6 | 7.5 | 154.146 | 0.42553 | 71.3336 | 6 | 7.5 | 227.6604 | 0.42553 | 40.4241 | 10 | 11.5 | 197.82 | 0.42553 | 36.7085 | 31 | 32.5 | 507.6707 |  |  | Living room | 0.70922 | 184.375 | 16 | 2092.1986
12 | 0.42553 | 114.428 | 8 | 9.5 | 462.5813 | 0.42553 | 93.2088 | 7 | 8.5 | 337.1384 | 0.42553 | 104.5213 | 12 | 13.5 | 600.4417 | 0.42553 | 51.0211 | 36 | 37.5 | 814.1669 | 0.42553 | 77.073 | 7 | 8.5 | 278.7746 | 0.42553 | 48.2991 | 8 | 9.5 | 195.2516 | 0.42553 | 71.3336 | 8 | 9.5 | 288.3699 | 0.42553 | 40.4241 | 12 | 13.5 | 232.2235 | 0.42553 | 36.7085 | 36 | 37.5 | 585.7739 |  |  | Kitchen/Dining | 0.70922 | 150.2113 | 16 | 1704.5248
13 | 0.42553 | 114.428 | 11 | 12.5 | 608.6596 | 0.42553 | 93.2088 | 11 | 12.5 | 495.7918 | 0.42553 | 104.5213 | 14 | 15.5 | 689.396 | 0.42553 | 51.0211 | 39 | 40.5 | 879.3002 | 0.42553 | 77.073 | 11 | 12.5 | 409.9627 | 0.42553 | 48.2991 | 11 | 12.5 | 256.91 | 0.42553 | 71.3336 | 11 | 12.5 | 379.434 | 0.42553 | 40.4241 | 14 | 15.5 | 266.627 | 0.42553 | 36.7085 | 39 | 40.5 | 632.6359 |  |  | Toilet 1 | 0.70922 | 43.3336 | 16 | 491.7288
14 | 0.42553 | 114.428 | 15 | 16.5 | 803.4307 | 0.42553 | 93.2088 | 14 | 15.5 | 614.7818 | 0.42553 | 104.5213 | 16 | 17.5 | 778.3503 | 0.42553 | 51.0211 | 39 | 40.5 | 879.3002 | 0.42553 | 77.073 | 14 | 15.5 | 508.3538 | 0.42553 | 48.2991 | 15 | 16.5 | 339.1213 | 0.42553 | 71.3336 | 15 | 16.5 | 500.8529 | 0.42553 | 40.4241 | 16 | 17.5 | 301.0304 | 0.42553 | 36.7085 | 39 | 40.5 | 632.6359 |  |  | Toilet 2 | 0.70922 | 43.3336 | 16 | 491.7288
15 | 0.42553 | 114.428 | 20 | 21.5 | 1046.8946 | 0.42553 | 93.2088 | 18 | 19.5 | 773.4351 | 0.42553 | 104.5213 | 19 | 20.5 | 911.7818 | 0.42553 | 51.0211 | 37 | 38.5 | 835.878 | 0.42553 | 77.073 | 18 | 19.5 | 639.5418 | 0.42553 | 48.2991 | 20 | 21.5 | 441.8853 | 0.42553 | 71.3336 | 20 | 21.5 | 652.6266 | 0.42553 | 40.4241 | 19 | 20.5 | 352.6357 | 0.42553 | 36.7085 | 37 | 38.5 | 601.3946 |  |  | Store | 0.70922 | 44.15 | 16 | 500.9929
16 | 0.42553 | 114.428 | 28 | 29.5 | 1436.4367 | 0.42553 | 93.2088 | 20 | 21.5 | 852.7618 | 0.42553 | 104.5213 | 21 | 22.5 | 1000.7361 | 0.42553 | 51.0211 | 36 | 37.5 | 814.1669 | 0.42553 | 77.073 | 20 | 21.5 | 705.1359 | 0.42553 | 48.2991 | 28 | 29.5 | 606.3077 | 0.42553 | 71.3336 | 28 | 29.5 | 895.4643 | 0.42553 | 40.4241 | 21 | 22.5 | 387.0391 | 0.42553 | 36.7085 | 36 | 37.5 | 585.7739
17 | 0.42553 | 114.428 | 37 | 38.5 | 1874.6717 | 0.42553 | 93.2088 | 22 | 23.5 | 932.0885 | 0.42553 | 104.5213 | 23 | 24.5 | 1089.6904 | 0.42553 | 51.0211 | 35 | 36.5 | 792.4558 | 0.42553 | 77.073 | 22 | 23.5 | 770.7299 | 0.42553 | 48.2991 | 37 | 38.5 | 791.2829 | 0.42553 | 71.3336 | 37 | 38.5 | 1168.6569 | 0.42553 | 40.4241 | 23 | 24.5 | 421.4426 | 0.42553 | 36.7085 | 35 | 36.5 | 570.1533
[43 empty] | 35 | 36.5 | 570.1533
Top Floor
Bedroom 1 :West wall | [5 empty] | Bedroom 1:South wall |  |  |  |  | Bedroom 2 : West Wall |  |  |  |  | Bedroom 2 : North wall |  |  |  |  | Puja Room : North Wall |  |  |  |  | Store room : North wall |  |  |  |  | Toilet 1 : East wall |  |  |  |  | Toilet 1 : South Wall |  |  |  |  | Toilet 2 : West wall |  |  |  |  | Toilet 2 : North wall |  |  |  |  | Bedroom 1 : Ceiling |  |  |  |  | Bedroom 2 : Ceiling |  |  |  |  | Puja : Ceiling |  |  |  |  | Toilet 1: Ceiling |  |  |  |  | Toilet 1: Ceiling |  |  |  |  | Toilet 2: Ceiling |  |  |  |  | Toilet 2: Ceiling
Time of day | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr) | U | Area (ft^2) | CLTD | Corrected CLTD | Q=U*A*Corr.CLTD(btu/hr)
10 | 0.42553 | 109.2296 | 4 | 5.5 | 255.6437 | 0.42553 | 73.3129 | 3 | 4.5 | 140.3864 | 0.42553 | 84.7087 | 4 | 5.5 | 198.2543 | 0.42553 | 100.063 | 7 | 8.5 | 361.9299 | 0.42553 | 22.5002 | 7 | 8.5 | 81.3837 | 0.42553 | 50.5577 | 7 | 8.5 | 182.8682 | 0.32154 | 50.0836 | 23.5 | 25 | 402.6009 | 0.32154 | 44.5835 | 3 | 4.5 | 64.5099 | 0.42553 | 42.3543 | 4 | 5.5 | 99.1271 | 0.42553 | 52.3127 | 7 | 8.5 | 189.2162 | 0.70922 | 137.8125 | 30 | 31.5 | 3078.7899 | 0.70922 | 135.375 | 30 | 31.5 | 3024.3351 | 0.70922 | 49.98 | 30 | 31.5 | 1116.5745 | 0.70922 | 49.98 | 30 | 31.5 | 1116.5745 | 0.70922 | 32.5 | 30 | 31.5 | 726.0638 | 0.70922 | 32.0625 | 30 | 31.5 | 716.2899 | 0.70922 | 22.68 | 30 | 31.5 | 506.6809
11 | 0.42553 | 109.2296 | 6 | 7.5 | 348.605 | 0.42553 | 93.2088 | 5 | 6.5 | 257.8117 | 0.42553 | 84.7087 | 6 | 7.5 | 270.3468 | 0.42553 | 100.063 | 10 | 11.5 | 489.6699 | 0.42553 | 22.5002 | 10 | 11.5 | 110.1074 | 0.42553 | 50.5577 | 10 | 11.5 | 247.41 | 0.32154 | 50.0836 | 32.5 | 34 | 547.5372 | 0.32154 | 44.5835 | 5 | 6.5 | 93.1809 | 0.42553 | 42.3543 | 6 | 7.5 | 135.1734 | 0.42553 | 52.3127 | 10 | 11.5 | 255.9984 | 0.70922 | 137.8125 | 48 | 49.5 | 4838.0984 | 0.70922 | 135.375 | 48 | 49.5 | 4752.5266 | 0.70922 | 49.98 | 48 | 49.5 | 1754.617 | 0.70922 | 49.98 | 48 | 49.5 | 1754.617 | 0.70922 | 32.5 | 48 | 49.5 | 1140.9574 | 0.70922 | 32.0625 | 48 | 49.5 | 1125.5984 | 0.70922 | 22.68 | 48 | 49.5 | 796.2128
12 | 0.42553 | 109.2296 | 8 | 9.5 | 441.5664 | 0.42553 | 93.2088 | 7 | 8.5 | 337.1384 | 0.42553 | 84.7087 | 8 | 9.5 | 342.4392 | 0.42553 | 100.063 | 12 | 13.5 | 574.8299 | 0.42553 | 22.5002 | 12 | 13.5 | 129.2565 | 0.42553 | 50.5577 | 12 | 13.5 | 290.4378 | 0.32154 | 50.0836 | 37.5 | 39 | 628.0574 | 0.32154 | 44.5835 | 7 | 8.5 | 121.852 | 0.42553 | 42.3543 | 8 | 9.5 | 171.2196 | 0.42553 | 52.3127 | 12 | 13.5 | 300.5199 | 0.70922 | 137.8125 | 64 | 65.5 | 6401.9282 | 0.70922 | 135.375 | 64 | 65.5 | 6288.6968 | 0.70922 | 49.98 | 64 | 65.5 | 2321.766 | 0.70922 | 49.98 | 64 | 65.5 | 2321.766 | 0.70922 | 32.5 | 64 | 65.5 | 1509.7518 | 0.70922 | 32.0625 | 64 | 65.5 | 1489.4282 | 0.70922 | 22.68 | 64 | 65.5 | 1053.5745
13 | 0.42553 | 109.2296 | 11 | 12.5 | 581.0084 | 0.42553 | 93.2088 | 11 | 12.5 | 495.7918 | 0.42553 | 84.7087 | 11 | 12.5 | 450.5779 | 0.42553 | 100.063 | 14 | 15.5 | 659.9898 | 0.42553 | 22.5002 | 14 | 15.5 | 148.4056 | 0.42553 | 50.5577 | 14 | 15.5 | 333.4656 | 0.32154 | 50.0836 | 40.5 | 42 | 676.3695 | 0.32154 | 44.5835 | 11 | 12.5 | 179.1941 | 0.42553 | 42.3543 | 11 | 12.5 | 225.289 | 0.42553 | 52.3127 | 14 | 15.5 | 345.0414 | 0.70922 | 137.8125 | 77 | 78.5 | 7672.5399 | 0.70922 | 135.375 | 77 | 78.5 | 7536.8351 | 0.70922 | 49.98 | 77 | 78.5 | 2782.5745 | 0.70922 | 49.98 | 77 | 78.5 | 2782.5745 | 0.70922 | 32.5 | 77 | 78.5 | 1809.3972 | 0.70922 | 32.0625 | 77 | 78.5 | 1785.0399 | 0.70922 | 22.68 | 77 | 78.5 | 1262.6809
14 | 0.42553 | 109.2296 | 15 | 16.5 | 766.9311 | 0.42553 | 93.2088 | 14 | 15.5 | 614.7818 | 0.42553 | 84.7087 | 15 | 16.5 | 594.7629 | 0.42553 | 100.063 | 16 | 17.5 | 745.1498 | 0.42553 | 22.5002 | 16 | 17.5 | 167.5547 | 0.42553 | 50.5577 | 16 | 17.5 | 376.4934 | 0.32154 | 50.0836 | 40.5 | 42 | 676.3695 | 0.32154 | 44.5835 | 14 | 15.5 | 222.2007 | 0.42553 | 42.3543 | 15 | 16.5 | 297.3814 | 0.42553 | 52.3127 | 16 | 17.5 | 389.5628 | 0.70922 | 137.8125 | 86 | 87.5 | 8552.1941 | 0.70922 | 135.375 | 86 | 87.5 | 8400.9309 | 0.70922 | 49.98 | 86 | 87.5 | 3101.5957 | 0.70922 | 49.98 | 86 | 87.5 | 3101.5957 | 0.70922 | 32.5 | 86 | 87.5 | 2016.844 | 0.70922 | 32.0625 | 86 | 87.5 | 1989.6941 | 0.70922 | 22.68 | 86 | 87.5 | 1407.4468
15 | 0.42553 | 109.2296 | 20 | 21.5 | 999.3344 | 0.42553 | 93.2088 | 18 | 19.5 | 773.4351 | 0.42553 | 84.7087 | 20 | 21.5 | 774.994 | 0.42553 | 100.063 | 19 | 20.5 | 872.8898 | 0.42553 | 22.5002 | 19 | 20.5 | 196.2783 | 0.42553 | 50.5577 | 19 | 20.5 | 441.0352 | 0.32154 | 50.0836 | 38.5 | 40 | 644.1614 | 0.32154 | 44.5835 | 18 | 19.5 | 279.5428 | 0.42553 | 42.3543 | 20 | 21.5 | 387.497 | 0.42553 | 52.3127 | 19 | 20.5 | 456.345 | 0.70922 | 137.8125 | 90 | 91.5 | 8943.1516 | 0.70922 | 135.375 | 90 | 91.5 | 8784.9734 | 0.70922 | 49.98 | 90 | 91.5 | 3243.383 | 0.70922 | 49.98 | 90 | 91.5 | 3243.383 | 0.70922 | 32.5 | 90 | 91.5 | 2109.0426 | 0.70922 | 32.0625 | 90 | 91.5 | 2080.6516 | 0.70922 | 22.68 | 90 | 91.5 | 1471.7872
16 | 0.42553 | 109.2296 | 28 | 29.5 | 1371.1798 | 0.42553 | 93.2088 | 20 | 21.5 | 852.7618 | 0.42553 | 84.7087 | 28 | 29.5 | 1063.3639 | 0.42553 | 100.063 | 21 | 22.5 | 958.0498 | 0.42553 | 22.5002 | 21 | 22.5 | 215.4274 | 0.42553 | 50.5577 | 21 | 22.5 | 484.063 | 0.32154 | 50.0836 | 37.5 | 39 | 628.0574 | 0.32154 | 44.5835 | 20 | 21.5 | 308.2139 | 0.42553 | 42.3543 | 28 | 29.5 | 531.682 | 0.42553 | 52.3127 | 21 | 22.5 | 500.8665 | 0.70922 | 137.8125 | 89 | 90.5 | 8845.4122 | 0.70922 | 135.375 | 89 | 90.5 | 8688.9628 | 0.70922 | 49.98 | 89 | 90.5 | 3207.9362 | 0.70922 | 49.98 | 89 | 90.5 | 3207.9362 | 0.70922 | 32.5 | 89 | 90.5 | 2085.9929 | 0.70922 | 32.0625 | 89 | 90.5 | 2057.9122 | 0.70922 | 22.68 | 89 | 90.5 | 1455.7021
17 | 0.42553 | 109.2296 | 37 | 38.5 | 1789.5058 | 0.42553 | 93.2088 | 22 | 23.5 | 932.0885 | 0.42553 | 84.7087 | 37 | 38.5 | 1387.78 | 0.42553 | 100.063 | 23 | 24.5 | 1043.2097 | 0.42553 | 22.5002 | 23 | 24.5 | 234.5766 | 0.42553 | 50.5577 | 23 | 24.5 | 527.0908 | 0.32154 | 50.0836 | 36.5 | 38 | 611.9533 | 0.32154 | 44.5835 | 22 | 23.5 | 336.885 | 0.42553 | 42.3543 | 37 | 38.5 | 693.89 | 0.42553 | 52.3127 | 23 | 24.5 | 545.388 | 0.70922 | 137.8125 | 82 | 83.5 | 8161.2367 | 0.70922 | 135.375 | 82 | 83.5 | 8016.8883 | 0.70922 | 49.98 | 82 | 83.5 | 2959.8085 | 0.70922 | 49.98 | 82 | 83.5 | 2959.8085 | 0.70922 | 32.5 | 82 | 83.5 | 1924.6454 | 0.70922 | 32.0625 | 82 | 83.5 | 1898.7367 | 0.70922 | 22.68 | 82 | 83.5 | 1343.1064
Partition Wall
Ground floor
Room | U | A | ΔT | Q=U*A*ΔT
Bedroom 1(E) . | 0.32154 | 109.2296 | 16 | 561.9528
Bedroom 1 (N) | 0.32154 | 77.5629 | 16 | 399.0373
Toilet (S) | 0.32154 | 67.5889 | 16 | 347.724
Bedroom 2(S) | 0.32154 | 67.9061 | 16 | 349.3561
Toilet(N) | 0.32154 | 59.7136 | 16 | 307.2082
Living Room (S) | 0.32154 | 73.8179 | 16 | 379.7703
Kitchen(N) | 0.32154 | 76.8228 | 16 | 395.2298
Living Room (E) | 0.32154 | 88.7875 | 16 | 456.7846
Passage(W) | 0.32154 | 37.1559 | 16 | 191.1557
Living Room(W) | 0.32154 | 76.8228 | 16 | 395.2298
Bedroom 2(E) | 0.32154 | 84.7087 | 16 | 435.8001
Kitchen(W) | 0.32154 | 114.4013 | 16 | 588.5595
First Floor
Room | U | A | ΔT | Q=U*A*ΔT
Bedroom( E) ,Kitchen (W) | 0.32154 | 114.428 | 16 | 588.6972
Bedrom (N) | 0.32154 | 96.2088 | 16 | 494.9651
Toilet 1 (S) | 0.32154 | 52.0836 | 16 | 267.9542
Living Room (W) | 0.32154 | 92.2087 | 16 | 474.3859
Toilet 1 (E) | 0.32154 | 48.2991 | 16 | 248.4841
Toilet 2 € | 0.32154 | 52.0836 | 16 | 267.9542
Living Room (S) | 0.32154 | 86.0213 | 16 | 442.5534
Kitchen (N), Store(S) | 0.32154 | 93.6469 | 16 | 481.7848
Toilet 1 North (Toilet 2 South) | 0.32154 | 63.4586 | 16 | 326.4751
Store West | 0.32154 | 25.3335 | 16 | 130.3331
Store North | 0.32154 | 78.7345 | 16 | 405.0648
Living Room East | 0.32154 | 88.7087 | 16 | 456.3794
Top Floor
Room | U | A | ΔT | Q=U*A*ΔT
Bedroom1(E) Toilet 1 (W) | 0.32154 | 82.2296 | 16 | 423.046
Bedroom 1 (N) | 0.32154 | 81.0629 | 16 | 417.0437
Bedroom 2 (E)Puja (W) | 0.32154 | 84.7087 | 16 | 435.8001
Bedroom 2 (S) | 0.32154 | 104.313 | 16 | 536.6584
Puja (E.) | 0.32154 | 74.2761 | 16 | 382.1279
Puja (S) | 0.32154 | 34.2502 | 16 | 176.2068
Store (E.) | 0.32154 | 12.9168 | 16 | 66.453
Store (W) | 0.32154 | 35.6668 | 16 | 183.4948
Store (S) | 0.32154 | 50.5577 | 16 | 260.1039
Toilet 1 (N) | 0.32154 | 25.3335 | 16 | 130.3331
Toilet 2 (E.) Passage (W) | 0.32154 | 42.3543 | 16 | 217.9001
Toilet 2 (N) | 0.32154 | 52.3127 | 16 | 269.133
Toilet 2 (S) | 0.32154 | 40.9377 | 16 | 210.6121
Passage (E) | 0.32154 | 16.5725 | 16 | 85.2603
Passage (N) | 0.32154 | 103.6097 | 16 | 533.0403
Passage (S) | 0.32154 | 126.3597 | 16 | 650.0821
Load Calculation for door(2'' wood)
Ground Floor (Door - 2 " wood)
Rooms | Door Type | R | U | Area | ΔT | Q=U*A*ΔT
Kitchen- Living Room | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Bedroom 1 | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Toilet | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Bedroom 2 | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Living Room- Passage | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
First Floor (Door - 2 " wood)
Rooms | Door Type | R | U | Area | ΔT | Q=U*A*ΔT
Toilet 1 | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Toilet 2 | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Living Room- Passage | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Store | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Bedroom | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Bedroom | SD | 2.39 | 0.41841 | 45 | 16 | 301.2552
Kitchen | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Kitchen | SD | 2.39 | 0.41841 | 45 | 16 | 301.2552
Top Floor (Door - 2 " wood)
Rooms | Door Type | R | U | Area | ΔT | Q=U*A*ΔT
Bedroom 2 | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Bedroom 1 | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Puja | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Toilet 1 | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Toilet 2 | D1 | 2.39 | 0.41841 | 19.25 | 16 | 128.8703
Passage | D | 2.39 | 0.41841 | 22.75 | 16 | 152.3013
Window load Calculation
Conduction heat transfer (Window W) | [5 empty] | Conduction heat transfer (Window W1) | [5 empty] | Conduction heat transfer (Window W2) | [5 empty] | Conduction heat transfer (Window W2)
Time fo the Day | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | Time fo the Day | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | Time fo the Day | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | Time fo the Day | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr)
10 | 0.54 | 27 | 4 | 5.5 | 80.19 | 10 | 0.54 | 31 | 4 | 5.5 | 92.07 | 10 | 0.54 | 7.875 | 4 | 5.5 | 23.3888 | 10 | 0.54 | 13.5 | 4 | 5.5 | 40.095
11 | 0.54 | 27 | 7 | 8.5 | 123.93 | 11 | 0.54 | 31 | 7 | 8.5 | 142.29 | 11 | 0.54 | 7.875 | 7 | 8.5 | 36.1463 | 11 | 0.54 | 13.5 | 7 | 8.5 | 61.965
12 | 0.54 | 27 | 9 | 10.5 | 153.09 | 12 | 0.54 | 31 | 9 | 10.5 | 175.77 | 12 | 0.54 | 7.875 | 9 | 10.5 | 44.6512 | 12 | 0.54 | 13.5 | 9 | 10.5 | 76.545
13 | 0.54 | 27 | 12 | 13.5 | 196.83 | 13 | 0.54 | 31 | 12 | 13.5 | 225.99 | 13 | 0.54 | 7.875 | 12 | 13.5 | 57.4087 | 13 | 0.54 | 13.5 | 12 | 13.5 | 98.415
14 | 0.54 | 27 | 13 | 14.5 | 211.41 | 14 | 0.54 | 31 | 13 | 14.5 | 242.73 | 14 | 0.54 | 7.875 | 13 | 14.5 | 61.6613 | 14 | 0.54 | 13.5 | 13 | 14.5 | 105.705
15 | 0.54 | 27 | 14 | 15.5 | 225.99 | 15 | 0.54 | 31 | 14 | 15.5 | 259.47 | 15 | 0.54 | 7.875 | 14 | 15.5 | 65.9137 | 15 | 0.54 | 13.5 | 14 | 15.5 | 112.995
16 | 0.54 | 27 | 14 | 15.5 | 225.99 | 16 | 0.54 | 31 | 14 | 15.5 | 259.47 | 16 | 0.54 | 7.875 | 14 | 15.5 | 65.9137 | 16 | 0.54 | 13.5 | 14 | 15.5 | 112.995
17 | 0.54 | 27 | 13 | 14.5 | 211.41 | 17 | 0.54 | 31 | 13 | 14.5 | 242.73 | 17 | 0.54 | 7.875 | 13 | 14.5 | 61.6613 | 17 | 0.54 | 13.5 | 13 | 14.5 | 105.705
Radiation heat transfer through window
Ground Floor
Bedroom 2 (W, North, Zone D) |  |  |  |  | Living Room (W, North, Zone C) |  |  |  |  | Bedroom 1 (W, South, Zone D) |  |  |  |  | Kitchen (W, South, Zone D) |  |  |  |  | Kitchen (W, East, Zone D) |  |  |  |  | Passage (W, South, Zone D)
TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL
10 | 27 | 0.81 | 27 | 590.49 | 10 | 27 | 0.81 | 30 | 656.1 | 10 | 27 | 0.81 | 59 | 1290.33 | 10 | 27 | 0.81 | 59 | 1290.33 | 10 | 27 | 0.81 | 124 | 2711.88 | 10 | 27 | 0.81 | 59 | 1290.33
11 | 27 | 0.81 | 29 | 634.23 | 11 | 27 | 0.81 | 33 | 721.71 | 11 | 27 | 0.81 | 67 | 1465.29 | 11 | 27 | 0.81 | 67 | 1465.29 | 11 | 27 | 0.81 | 110 | 2405.7 | 11 | 27 | 0.81 | 67 | 1465.29
12 | 27 | 0.81 | 31 | 677.97 | 12 | 27 | 0.81 | 34 | 743.58 | 12 | 27 | 0.81 | 69 | 1509.03 | 12 | 27 | 0.81 | 69 | 1509.03 | 12 | 27 | 0.81 | 85 | 1858.95 | 12 | 27 | 0.81 | 69 | 1509.03
13 | 27 | 0.81 | 32 | 699.84 | 13 | 27 | 0.81 | 35 | 765.45 | 13 | 27 | 0.81 | 63 | 1377.81 | 13 | 27 | 0.81 | 63 | 1377.81 | 13 | 27 | 0.81 | 65 | 1421.55 | 13 | 27 | 0.81 | 63 | 1377.81
14 | 27 | 0.81 | 31 | 677.97 | 14 | 27 | 0.81 | 34 | 743.58 | 14 | 27 | 0.81 | 52 | 1137.24 | 14 | 27 | 0.81 | 52 | 1137.24 | 14 | 27 | 0.81 | 60 | 1312.2 | 14 | 27 | 0.81 | 52 | 1137.24
15 | 27 | 0.81 | 30 | 656.1 | 15 | 27 | 0.81 | 32 | 699.84 | 15 | 27 | 0.81 | 41 | 896.67 | 15 | 27 | 0.81 | 41 | 896.67 | 15 | 27 | 0.81 | 57 | 1246.59 | 15 | 27 | 0.81 | 41 | 896.67
16 | 27 | 0.81 | 28 | 612.36 | 16 | 27 | 0.81 | 29 | 634.23 | 16 | 27 | 0.81 | 36 | 787.32 | 16 | 27 | 0.81 | 36 | 787.32 | 16 | 27 | 0.81 | 53 | 1159.11 | 16 | 27 | 0.81 | 36 | 787.32
17 | 27 | 0.81 | 29 | 634.23 | 17 | 27 | 0.81 | 29 | 634.23 | 17 | 27 | 0.81 | 30 | 656.1 | 17 | 27 | 0.81 | 30 | 656.1 | 17 | 27 | 0.81 | 48 | 1049.76 | 17 | 27 | 0.81 | 30 | 656.1
First Floor
Living room, North, W, Zone D |  |  |  |  | Toilet 2 , North, W2, Zone D |  |  |  |  | Toilet 1, North, W2, Zone D |  |  |  |  | Store, East, W2, Zone D |  |  |  |  | Kitchen, East, W, Zone C |  |  |  |  | Kitchen, South, W, Zone C |  |  |  |  | Kitchen, South, W1, Zone C |  |  |  |  | Bedroom, South, W, Zone D |  |  |  |  | Passage, East, W, Zone D
Time of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | Time of day | A | SC | SCL | Q=A*SC*SCL | Time of day | A | SC | SCL | Q=A*SC*SCL | Time of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL
10 | 27 | 0.81 | 30 | 656.1 | 10 | 7.75 | 0.81 | 27 | 169.4925 | 10 | 7.75 | 0.81 | 30 | 188.325 | 10 | 7.75 | 0.81 | 110 | 690.525 | 10 | 27 | 0.81 | 124 | 2711.88 | 10 | 27 | 0.81 | 54 | 1180.98 | 10 | 31 | 0.81 | 54 | 1355.94 | 10 | 27 | 0.81 | 54 | 1180.98 | 10 | 27 | 0.81 | 110 | 2405.7
11 | 27 | 0.81 | 33 | 721.71 | 11 | 7.75 | 0.81 | 29 | 182.0475 | 11 | 7.75 | 0.81 | 33 | 207.1575 | 11 | 7.75 | 0.81 | 85 | 533.5875 | 11 | 27 | 0.81 | 89 | 1946.43 | 11 | 27 | 0.81 | 70 | 1530.9 | 11 | 31 | 0.81 | 70 | 1757.7 | 11 | 27 | 0.81 | 70 | 1530.9 | 11 | 27 | 0.81 | 85 | 1858.95
12 | 27 | 0.81 | 34 | 743.58 | 12 | 7.75 | 0.81 | 31 | 194.6025 | 12 | 7.75 | 0.81 | 34 | 213.435 | 12 | 7.75 | 0.81 | 65 | 408.0375 | 12 | 27 | 0.81 | 62 | 1355.94 | 12 | 27 | 0.81 | 79 | 1727.73 | 12 | 31 | 0.81 | 79 | 1983.69 | 12 | 27 | 0.81 | 79 | 1727.73 | 12 | 27 | 0.81 | 65 | 1421.55
13 | 27 | 0.81 | 35 | 765.45 | 13 | 7.75 | 0.81 | 32 | 200.88 | 13 | 7.75 | 0.81 | 35 | 219.7125 | 13 | 7.75 | 0.81 | 60 | 376.65 | 13 | 27 | 0.81 | 56 | 1224.72 | 13 | 27 | 0.81 | 79 | 1727.73 | 13 | 31 | 0.81 | 79 | 1983.69 | 13 | 27 | 0.81 | 79 | 1727.73 | 13 | 27 | 0.81 | 60 | 1312.2
14 | 27 | 0.81 | 34 | 743.58 | 14 | 7.75 | 0.81 | 31 | 194.6025 | 14 | 7.75 | 0.81 | 34 | 213.435 | 14 | 7.75 | 0.81 | 57 | 357.8175 | 14 | 27 | 0.81 | 52 | 1137.24 | 14 | 27 | 0.81 | 70 | 1530.9 | 14 | 31 | 0.81 | 70 | 1757.7 | 14 | 27 | 0.81 | 70 | 1530.9 | 14 | 27 | 0.81 | 57 | 1246.59
15 | 27 | 0.81 | 32 | 699.84 | 15 | 7.75 | 0.81 | 30 | 188.325 | 15 | 7.75 | 0.81 | 32 | 200.88 | 15 | 7.75 | 0.81 | 53 | 332.7075 | 15 | 27 | 0.81 | 47 | 1027.89 | 15 | 27 | 0.81 | 54 | 1180.98 | 15 | 31 | 0.81 | 54 | 1355.94 | 15 | 27 | 0.81 | 54 | 1180.98 | 15 | 27 | 0.81 | 53 | 1159.11
16 | 27 | 0.81 | 29 | 634.23 | 16 | 7.75 | 0.81 | 28 | 175.77 | 16 | 7.75 | 0.81 | 29 | 182.0475 | 16 | 7.75 | 0.81 | 48 | 301.32 | 16 | 27 | 0.81 | 43 | 940.41 | 16 | 27 | 0.81 | 40 | 874.8 | 16 | 31 | 0.81 | 40 | 1004.4 | 16 | 27 | 0.81 | 40 | 874.8 | 16 | 27 | 0.81 | 48 | 1049.76
17 | 27 | 0.81 | 29 | 634.23 | 17 | 7.75 | 0.81 | 29 | 182.0475 | 17 | 7.75 | 0.81 | 29 | 182.0475 | 17 | 7.75 | 0.81 | 43 | 269.9325 | 17 | 27 | 0.81 | 37 | 809.19 | 17 | 27 | 0.81 | 33 | 721.71 | 17 | 31 | 0.81 | 33 | 828.63 | 17 | 27 | 0.81 | 33 | 721.71 | 17 | 27 | 0.81 | 43 | 940.41
Top Floor
Toilet 2, North, W2, Zone C |  |  |  |  | Bedroom 2, North, W, Zone D |  |  |  |  | Puja, North, W1, Zone C |  |  |  |  | Bedroom 1, South, W, Zone D |  |  |  |  | Toilet 1, East, W2, Zone D |  |  |  |  | Bedroom 1, East, W, Zone D1 |  |  |  |  | Passage, East, W1, Zone C |  |  |  |  | Passage, South, W1, Zone C (X2)
TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL | TIme of day | A | SC | SCL | Q=A*SC*SCL
10 | 7.875 | 0.81 | 30 | 191.3625 | 10 | 27 | 0.81 | 27 | 590.49 | 10 | 31 | 0.81 | 30 | 753.3 | 10 | 27 | 0.81 | 46 | 1006.02 | 10 | 7.875 | 0.81 | 110 | 701.6625 | 10 | 31 | 0.81 | 110 | 2762.1 | 10 | 31 | 0.81 | 124 | 3113.64 | 10 | 31 | 0.81 | 54 | 1355.94
11 | 7.875 | 0.81 | 33 | 210.4988 | 11 | 27 | 0.81 | 29 | 634.23 | 11 | 31 | 0.81 | 33 | 828.63 | 11 | 27 | 0.81 | 59 | 1290.33 | 11 | 7.875 | 0.81 | 85 | 542.1938 | 11 | 31 | 0.81 | 85 | 2134.35 | 11 | 31 | 0.81 | 89 | 2234.79 | 11 | 31 | 0.81 | 70 | 1757.7
12 | 7.875 | 0.81 | 34 | 216.8775 | 12 | 27 | 0.81 | 31 | 677.97 | 12 | 31 | 0.81 | 34 | 853.74 | 12 | 27 | 0.81 | 67 | 1465.29 | 12 | 7.875 | 0.81 | 65 | 414.6187 | 12 | 31 | 0.81 | 65 | 1632.15 | 12 | 31 | 0.81 | 62 | 1556.82 | 12 | 31 | 0.81 | 79 | 1983.69
13 | 7.875 | 0.81 | 35 | 223.2562 | 13 | 27 | 0.81 | 32 | 699.84 | 13 | 31 | 0.81 | 35 | 878.85 | 13 | 27 | 0.81 | 69 | 1509.03 | 13 | 7.875 | 0.81 | 60 | 382.725 | 13 | 31 | 0.81 | 60 | 1506.6 | 13 | 31 | 0.81 | 56 | 1406.16 | 13 | 31 | 0.81 | 79 | 1983.69
14 | 7.875 | 0.81 | 34 | 216.8775 | 14 | 27 | 0.81 | 31 | 677.97 | 14 | 31 | 0.81 | 34 | 853.74 | 14 | 27 | 0.81 | 63 | 1377.81 | 14 | 7.875 | 0.81 | 57 | 363.5888 | 14 | 31 | 0.81 | 57 | 1431.27 | 14 | 31 | 0.81 | 52 | 1305.72 | 14 | 31 | 0.81 | 70 | 1757.7
15 | 7.875 | 0.81 | 32 | 204.12 | 15 | 27 | 0.81 | 30 | 656.1 | 15 | 31 | 0.81 | 32 | 803.52 | 15 | 27 | 0.81 | 52 | 1137.24 | 15 | 7.875 | 0.81 | 53 | 338.0738 | 15 | 31 | 0.81 | 53 | 1330.83 | 15 | 31 | 0.81 | 47 | 1180.17 | 15 | 31 | 0.81 | 54 | 1355.94
16 | 7.875 | 0.81 | 29 | 184.9837 | 16 | 27 | 0.81 | 28 | 612.36 | 16 | 31 | 0.81 | 29 | 728.19 | 16 | 27 | 0.81 | 41 | 896.67 | 16 | 7.875 | 0.81 | 48 | 306.18 | 16 | 31 | 0.81 | 48 | 1205.28 | 16 | 31 | 0.81 | 43 | 1079.73 | 16 | 31 | 0.81 | 40 | 1004.4
17 | 7.875 | 0.81 | 29 | 184.9837 | 17 | 27 | 0.81 | 29 | 634.23 | 17 | 31 | 0.81 | 29 | 728.19 | 17 | 27 | 0.81 | 36 | 787.32 | 17 | 7.875 | 0.81 | 43 | 274.2862 | 17 | 31 | 0.81 | 43 | 1079.73 | 17 | 31 | 0.81 | 37 | 929.07 | 17 | 31 | 0.81 | 33 | 828.63
Occupant load
Floor | Rooms | No. of People (N) | CLF | QS(Moderately Active) | Sensible Heat Gain = N*QS*CLF | QL | Latent Heat Gain=N*QL | Total Q=SHG+LHG (btu/hr)
Ground Floor | Bedroom 1 | 2 | 1 | 250 | 500 | 200 | 400 | 900
| Bedroom 2 | 1 | 1 | 250 | 250 | 200 | 200 | 450
| Living room | 3 | 1 | 250 | 750 | 200 | 600 | 1350
| Kitchen/Dining | 3 | 1 | 250 | 750 | 200 | 600 | 1350
First Floor | Bedroom | 2 | 1 | 250 | 500 | 200 | 400 | 900
| Store | 1 | 1 | 250 | 250 | 200 | 200 | 450
| Living room | 3 | 1 | 250 | 750 | 200 | 600 | 1350
| Kitchen/Dining | 3 | 1 | 250 | 750 | 200 | 600 | 1350
Top Floor | Bedroom 1 | 2 | 1 | 250 | 500 | 200 | 400 | 900
| Bedroom 2 | 1 | 1 | 250 | 250 | 200 | 200 | 450
Lighting Load
Ground Floor
Room | Type of Bulb | No. of Lights | Wattage | Ballast Factor | Q=N*W*fb(Watt) | Q(Btu/hr)
Kitchen | CFL | 1 | 6 | 1.2 | 7.2 | 24.552
Bedroom 1 | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Bedroom2 | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Living Room | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Passage | Fluorescent tube | 1 | 40 | 1.2 | 48 | 163.68
First Floor
Room | Type of Bulb | No. of Lights | Wattage | Ballast Factor | Q=N*W*fb(Watt) | Q(Btu/hr)
Bedroom | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Living Room | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Kitchen/ Dining | CFL | 1 | 6 | 1.2 | 7.2 | 24.552
Store | Fluorescent tube | 1 | 40 | 1.2 | 48 | 163.68
Passage | Fluorescent tube | 1 | 40 | 1.2 | 48 | 163.68
Top Floor
Room | Type of Bulb | No. of Lights | Wattage | Ballast Factor | Q=N*W*fb(Watt) | Q(Btu/hr)
Bedroom 1 | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Bedroom 2 | Fluorescent tube | 2 | 40 | 1.2 | 96 | 327.36
Puja | CFL | 1 | 6 | 1.2 | 7.2 | 24.552
Store | Fluorescent tube | 1 | 40 | 1.2 | 48 | 163.68
Passage | Fluorescent tube | 1 | 40 | 1.2 | 48 | 163.68
Equipment Load
Ground Floor |  |  |  |  | First Floor |  |  |  |  | Top Floor
Bedroom1 | Watt | Usage Factor | btu conversion | Q(btu/hr) | Bedroom | Watt | Usage Factor | btu conversion | Q(btu/hr) | Bedroom1 | Watt | Usage Factor | btu conversion | Q(btu/hr)
Laptop | 60 | 0.58333 | 3.41 | 119.35 | Laptop | 60 | 0.33333 | 3.41 | 68.2 | Laptop | 60 | 0.33333 | 3.41 | 68.2
Mobile | 33 | 0.66667 | 3.41 | 75.02 | Mobile | 33 | 0.5 | 3.41 | 56.265 | Mobile | 33 | 0.5 | 3.41 | 56.265
Hair dryer | 1200 | 0.020833 | 3.41 | 85.25 | Hair dryer | 1200 | 0.010417 | 3.41 | 42.625 | Hair dryer | 1200 | 0.010417 | 3.41 | 42.625
|  |  | total | #VALUE! |  |  |  | Total | 167.09 |  |  |  | Total | 167.09
279.62
Bedroom 2 | Watt | Usage Factor | btu conversion | Q(btu/hr) | Living Room | Watt | Usage Factor | btu conversion | Q(btu/hr) | Bedroom 2 | Watt | Usage Factor | btu conversion | Q(btu/hr)
Laptop | 60 | 0.33333 | 3.41 | 68.2 | Laptop | 60 | 0.33333 | 3.41 | 68.2 | Laptop | 60 | 0.33333 | 3.41 | 68.2
Mobile | 33 | 0.5 | 3.41 | 56.265 | Mobile | 33 | 0.5 | 3.41 | 56.265 | Mobile | 33 | 0.5 | 3.41 | 56.265
Hair dryer | 1200 | 0.010417 | 3.41 | 42.625 | Television | 120 | 0.16667 | 3.41 | 68.2 | Hair dryer | 1200 | 0.010417 | 3.41 | 42.625
|  |  | Total | 167.09 |  |  |  | Total | 192.665 |  |  |  | Total | 167.09
Living Room | Watt | Usage Factor | btu conversion | Q(btu/hr) | Kitchen | Watt | Usage Factor | btu conversion | Q(btu/hr)
Laptop | 60 | 0.33333 | 3.41 | 68.2 | Coffee Brewer | 480 | 0.020833 | 3.41 | 34.1
Mobile | 33 | 0.5 | 3.41 | 56.265 | Dishwasher | 1660 | 0.041667 | 3.41 | 235.8583
Television | 120 | 0.16667 | 3.41 | 68.2 | Microwave | 380 | 0.020833 | 3.41 | 26.9958
|  |  | Total | 192.665 | Refrigerator | 1400 | 0.66667 | 3.41 | 3182.6667
[5 empty] | Toaster | 2470 | 0.010417 | 3.41 | 87.7365
Kitchen | Watt | Usage Factor | btu conversion | Q(btu/hr) | Stove | 11700 | 0.125 | 3.1 | 4533.75
Coffee Brewer | 480 | 0.020833 | 3.41 | 34.1 |  |  |  | total | 8101.1073
Dishwasher | 1660 | 0.041667 | 3.41 | 235.8583
Microwave | 380 | 0.020833 | 3.41 | 26.9958
Refrigerator | 1400 | 0.66667 | 3.41 | 3182.6667
Toaster | 2470 | 0.010417 | 3.41 | 87.7365
Stove | 11700 | 0.125 | 3.1 | 4533.75
|  |  | Total | 8101.1073

## Total Load Calculation
Total load calculation
Ground floor
Bedroom 1
West wall |  |  | Partition wall N | [5 empty] | South wall |  |  | Partition wall E |  |  |  | Roof | Window Conduction |  |  |  |  | Window Radiation |  |  |  | Door |  |  |  |  | Occupant |  |  |  | lighting |  |  |  | Equipment | Total(Btu/hr) | Total(tr)
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT |  |  | Q | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | Q | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | 7574.2457 | 0.63119
37 | 38.5 | 1789.5058 | 0.32154 | 77.5629 | 16 |  |  | 399.0373 | 22 | 23.5 | 733.1287 | 0.32154 | 109.2296 | 16 | 561.9528 | 1563.8298 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 30 | 656.1 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 2 | 500 | 400 | 900 | 2 | 40 | 1.2 | 327.36 | 279.62
Volume | 1228.8327
Infiltration airflow(cfm) | 10.2403
Bedroom 2
West |  |  | Partition S | [5 empty] | North |  |  | Partition wall E U: Partition E; Roof Q: Roof; Window Conduction U: WIndow Conduction |  |  | Window Radiaion |  |  |  | Door |  |  |  |  | Occupant |  |  |  | Lighting |  |  |  | Equipment | total(btu/hr) | Total(tons)
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT |  |  | Q | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q |  | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | 5874.9931 | 0.48958
37 | 38.5 | 1387.78 | 0.32154 | 67.9061 | 16 |  |  | 349.3561 | 23 | 24.5 | 663.6486 | 0.32154 | 84.7087 | 16 | 435.8001 | 1096.017 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 29 | 634.23 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 1 | 250 | 200 | 450 | 2 | 40 | 1.2 | 327.36 | 167.09
Volume | 816.2328
Infiltration airflow(cfm) | 6.8019
Living room
North |  |  | Partition S | [5 empty] | Partition E |  |  | Partition wall E A: Partition W; Window Conduction U: Roof; Window Conduction A: WIndow conduction |  |  |  | Window radiation |  |  |  | Door 1 |  |  |  |  | Door 2 |  |  |  |  | Occupant |  |  |  | Lighting |  |  |  | Equipment | Total
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT |  |  | Q | U | A | ΔT | Q | U | A | ΔT | Q |  | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | Q(btu/hr) | Q(tr)
23 | 24.5 | 725.282 | 0.32154 | 73.8179 | 16 |  |  | 379.7703 | 0.32154 | 88.7875 | 16 | 456.7846 | 0.32154 | 76.8228 | 16 | 395.2298 | 1536.1702 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 29 | 634.23 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 3 | 750 | 600 | 1350 | 2 | 40 | 1.2 | 327.36 | 192.665 | 6513.5044 | 0.54279
Volume | 1207.0983
Infiltration airflow(cfm) | 10.0592
Kitchen
South wall |  |  | East wall |  |  | Partition N |  |  |  | Partition W |  | Partition wall E ΔT: Roof; Partition wall E Q: Window Conduction | WIndow Radiation South |  |  |  | WIndow Radiation East |  |  |  | Door |  |  |  |  | Occupant |  |  |  |  | Lighting |  |  | Equipment | Total(Btu/hr) | Total Q(tr)
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | U | A | ΔT | Q |  | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | 16238.0452 | 1.3532
22 | 23.5 | 725.7279 | 35 | 36.5 | 1357.5089 | 0.32154 | 76.8228 | 16 | 395.2298 | 0.32154 | 114.4013 | 16 | 588.5595 | 1625.7885 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 30 | 656.1 | 27 | 0.81 | 48 | 1049.76 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 3 | 750 | 600 | 1350 | 1 | 6 | 1.2 | 24.552 | 8101.1073
Volume | 1277.5189
Infiltration airflow(cfm) | 10.646
First floor
Bedroom
West wall |  |  | south wall |  |  | Partition N U: Partition E; Partition W U: Partition N | Roof | WIndow Conduction |  |  |  |  | Window radiation |  |  |  | Door |  |  |  |  | Door (SD) |  |  |  |  | Occupant |  |  |  | Lighting |  |  |  | Equipment | Total
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | U | A | ΔT | Q | Q | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | Q (btu/hr) | Q(tr)
37 | 38.5 | 1874.6717 | 22 | 23.5 | 932.0885 | 0.32154 | 114.428 | 16 | 588.6972 | 0.32154 | 96.2088 | 16 | 494.9651 | 2257.1518 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 33 | 721.71 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 2 | 500 | 400 | 900 | 2 | 40 | 1.2 | 4.092 | 167.09 | 8456.4788 | 0.70471
Volume | 1773.6342
Infiltration airflow(cfm) | 14.7803
Living room
North |  |  | Partition E |  |  | Partition E A: Partition W; Partition N A: Partition S; WIndow Conduction U: Roof; WIndow Conduction A: Window Conduction |  |  |  | Window Radiation |  |  |  | Door(D-3) |  |  |  |  | Occupant |  |  |  | Lighting |  |  |  | Equipment | Total
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | U | A | ΔT | Q | U | A | ΔT | Q | Q | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | Q(btu/hr) | Q(tr)
23 | 24.4 | 1089.6904 | 0.32154 | 88.7087 | 16 | 456.3794 | 0.32154 | 92.2087 | 16 | 474.3859 | 0.32154 | 86.0213 | 16 | 442.5534 | 2092.1986 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 29 | 634.23 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 3 | 750 | 600 | 1350 | 2 | 40 | 1.2 | 4.092 | 192.665 | 7404.5085 | 0.61704
Volume | 1644.0166
Infiltration airflow(cfm) | 13.7001
Kitchen
east |  |  | Partition E U: south; Partition E Q: Partition N; Partition W Q: Partition W; Partition S Q: Roof; Roof Q: Window conduction(W) |  | Windwow Radiation(W) |  |  |  | Window Conduction(W1) |  |  |  |  | Windwow Radiation(W1) |  |  |  | Door (D) |  |  |  |  | Door (SD) |  |  |  |  | Occupant |  |  |  | Lighting |  |  |  | Equipment | Total
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | U | A | ΔT | Q | Q | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | R | U | Area | ΔT | Q=U*A*ΔT | R | U | Area | ΔT | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) |  | Q(btu/hr) | Q(tr)
35 | 36.5 | 792.4558 | 22 | 23.5 | 770.7299 | 0.32154 | 93.6469 | 16 | 481.7848 | 0.32154 | 114.428 | 16 | 588.6972 | 1704.5248 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 37 | 809.19 | 0.54 | 31 | 13 | 14.5 | 242.73 | 31 | 0.81 | 33 | 828.63 | 2.39 | 0.41841 | 22.75 | 16 | 152.3013 | 2.39 | 0.41841 | 45 | 16 | 301.2552 | 3 | 750 | 600 | 1350 | 1 | 6 | 1.2 | 4.092 | 8101.1073 | 16338.9082 | 1.3616
Volume | 1339.3887
Infiltration airflow(cfm) | 11.1616
Top floor
Bedroom 1
West wall |  |  | South wall |  |  | Partition N U: Partition wall E; Partition W U: Partition wall N; Roof Q: Roof; Window conduction(W) U: WIndow Conduction W(2) |  |  | Windwo radiation |  |  |  | Door |  |  |  | Occupant |  |  |  | Lighting |  |  |  | Equipment | Total
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | U | A | ΔT | Q | Q | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | Area | R | U | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) | Q | Q Btu/hr) | Q(TR)
37 | 38.5 | 1789.5058 | 22 | 23.5 | 932.0885 | 0.32154 | 82.2296 | 16 | 423.046 | 0.32154 | 81.0629 | 16 | 417.0437 | 8161.2367 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 36 | 787.32 | 22.75 | 2.39 | 0.41841 | 152.3013 | 2 | 500 | 400 | 900 | 2 | 40 | 1.2 | 327.36 | 167.09 | 14268.402 | 1.189
Volume | 1228.8327
Infiltration airflow(cfm) | 10.2403
Bedroom 2
West wall |  |  | North wall |  |  | Partition wall E U: Bedroom 2 East(Puja West); Partition wall N U: Bedroom 2 South; Roof Q: Roof; WIndow Conduction W(2) U: Window Conduction W (N) |  |  | WIndow Radiation |  |  |  | Door |  |  |  | occupant load |  |  |  | Lighting load |  |  |  | Equipment load | Total
CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | U | A | ΔT | Q | U | A | ΔT | Q | Q | U | A | CLTD | Corrected CLTD | Q=U*A* Corr.CLTD(btu/hr) | A | SC | SCL | Q=A*SC*SCL | Area | R | U | Q=U*A*ΔT | No of people | Sensible Heat Gain= N*QS*CLF | Latent Heat Gain= N*QL | Total Q=SHG+LHG | No. of lights | Wattage(W) | Ballast factor(fb) | Q(Btu/hr) | Q | Q(Btu/hr) | Q(TR)
37 | 38.5 | 1387.78 | 23 | 24.5 | 1043.2097 | 0.32154 | 84.7087 | 16 | 435.8001 | 0.32154 | 104.313 | 16 | 536.6584 | 8016.8883 | 0.54 | 27 | 13 | 14.5 | 211.41 | 27 | 0.81 | 29 | 634.23 | 22.75 | 2.39 | 0.41841 | 152.3013 | 1 | 250 | 200 | 450 | 2 | 40 | 1.2 | 327.36 | 167.09 | 13362.7278 | 1.1136
Volume | 1207.0983
Infiltration airflow(cfm) | 10.0592
Parameters | Q(btu/hr) | Q(TR) | Safety factor(10%)
East | 435.8001 | 0.036317 | 0.039948
West | 1387.78 | 0.11565 | 0.12721
North | 1043.2097 | 0.086934 | 0.095628
South | 536.6584 | 0.044722 | 0.049194
Roof | 8016.8883 | 0.66807 | 0.73488
Door | 152.3013 | 0.012692 | 0.013961
Window | 845.64 | 0.07047 | 0.077517
Occupant | 450 | 0.0375 | 0.04125
Lighting | 327.36 | 0.02728 | 0.030008
Equipment | 167.09 | 0.013924 | 0.015317
Total | 13362.7278 | 1.1136 | 1.2249

## Sheet2
CFM
Ground Floor | [6 empty] | First Floor | [5 empty] | Top Floor
Room | Ton | cfm | Infilteration cfm | Total cfm | Total Ton | Duct Size | Room | Ton | cfm | Infilteration cfm | Total cfm | Total Ton | Room | Ton | cfm | Infilteration cfm | Total cfm | Total Ton
Bedroom 1 | 0.63119 | 237.7682 | 10.2403 | 248.0085 | 0.65837 | 6*10 | Bedroom | 0.70471 | 265.463 | 14.7803 | 280.2432 | 0.74394 | Bedroom 1 | 1.189 | 447.9089 | 10.2403 | 458.1492 | 1.2162
Bedroom 2 | 0.48958 | 184.4258 | 6.8019 | 191.2278 | 0.50764 | 6*8 | Living Room | 0.61704 | 232.4399 | 13.7001 | 246.14 | 0.65341 | Bedroom 2 | 1.1136 | 419.4783 | 10.0592 | 429.5374 | 1.1403
Living Room | 0.54279 | 204.4698 | 10.0592 | 214.5289 | 0.5695 | 6*9 | Kitchen | 1.3616 | 512.9056 | 11.1616 | 524.0671 | 1.3912 | Total | 2.3026 | 867.3872 | 20.2994 | 887.6866 | 2.3565
Kitchen | 1.3532 | 509.7393 | 10.646 | 520.3853 | 1.3814
Total | 3.0167 | 1136.4031 | 37.7474 | 1174.1504 | 3.1169 | 8*24
| Ton | cfm
| #REF! | #REF!
add 10% | #REF!
AC | Ton | cfm
| 9 | 3390.3

## Sheet3
Ground Floor |  |  |  | First Floor |  |  |  | Top Floor
Room | Ton | add 10% | AC | Room | Ton | add 10% | AC | Room | Ton | add 10% | AC
Bedroom 1 | 0.65837 | 0.72421 | 0.75 | Bedroom | 0.74394 | 0.81834 | 1 | Bedroom 1 | 1.2162 | 1.3378 | 1.5
Bedroom 2 | 0.50764 | 0.5584 | 0.75 | Living Room | 0.65341 | 0.71875 | 0.75 | Bedroom 2 | 1.1403 | 1.2543 | 1.5
Living Room | 0.5695 | 0.62644 | 0.75 | Kitchen | 1.3912 | 1.5303 | 1.5
Kitchen | 1.3814 | 1.5196 | 1.5
Ground Foor
Room | AC Capacity (TR) | AC type
Bedroom 1 | 0.75 | Split AC wall mount inverter type
Bedroom 2 | 0.75 | Split AC wall mount inverter type
Living Room | 0.75 | Split AC wall mount inverter type
Kitchen | 1.5 | Split AC wall mount inverter type
First Foor
Room | AC Capacity (TR) | AC type
Bedroom | 1 | Split AC wall mount inverter type
Living Room | 0.75 | Split AC wall mount inverter type
Kitchen | 1.5 | Split AC wall mount inverter type
Top Foor
Room | AC Capacity (TR) | AC type
Bedroom 1 | 1.5 | Split AC wall mount inverter type
Bedroom 2 | 1.5 | Split AC wall mount inverter type